**Performance of a Full-Scale Activated Sludge Process for Sakket ( Musrata – Libya) Municipal Wastewater Treatment Plant**

Khaled Shahot1, Ibtesam Habib2 and Ahmed Ekhmaj3

1. Department of Civil Engineering, Faculty of Engineering, Almergib University Khom-Libya

2. Department of Environment and Water Resources, Faculty of Technical Engineering Masalata – Libya

3.Soil and Water Department, Faculty of Agriculture, University of Tripoli, Libya

[kmshahot@gmail.com1](mailto:kmshahot@gmail.com1), [ibteshahot@gmail.com2](mailto:ibteshahot@gmail.com2), [ekhmaj@gmail.com3](mailto:ekhmaj@gmail.com3)

**Abstract:** The study aimed to evaluate the effects of temperature and sampling time on the efficiency of remove the organic matter and the suspended solids from Musrata municipal wastewater treatment plant. Many laboratory experiments have been conducted to determine parameters such as BOD5, COD, TSS and VTSS. The samples of water were collected before and after treating wastewater by means of activated sludge process among different time of the day i.e., 9a.m, 11a.m and 1p.m, with the temperature ranges between (10-20)oC and (25-30)oC during February and November 2011, respectively. The results revealed that at 16oC during February the removal percentage of BOD5, COD, TSS and VTSS were 90%, 80%, 80% and 89%, respectively. At 28oC during November, the removal percentage of BOD5, COD, TSS and VTSS were 90%, 85% and 85% and 86%, respectively .Such results successfully verified the significance of using the activated sludge process to treat wastewater in both warm and cold area.

[Khaled Shahot, Ibtesam Habib and Ahmed Ekhmaj. **Performance of a Full-Scale Activated Sludge Process for Sakket (Musrata – Libya) Municipal Wastewater Treatment Plant.** *N Y Sci J* 2015;8(10):34-37]. (ISSN: 1554-0200). <http://www.sciencepub.net/newyork>. 7

**Keywords:** biological treatment, Activated sludge, wastewater treatment, organic removal, suspended solids removal.

1. **Introduction**

Used water is a form of wastewater that is made up of various substances such as food scraps, human waste, soaps, oil, chemicals and domestic wastes. The sewage’s flow usually goes through a huge underground pipe network to wastewater treatment place as that is where the treatment of contaminated water is carried out using different ways for pollutant removal. Sewage treatment is crucial as there is a scarcity of natural water resources and the higher demand for supply of clean water. Furthermore, huge volumes of wastewater being sent back to the natural water resources will affect the source’s water quality.

These matters put an emphasis on water development’s technology. Organic matter (BOD5/COD) and total suspended solids (TSS) are the base pollutants present in municipal wastewater with a potential of causing deleterious effects to public health and the environment. Several methods have been applied in conventional wastewater treatment technologies to remove these pollutants (Metcalf and Eddy, 2003).

In this regard, specific attention is essential to evaluate current wastewater treatment amenities’ impact on environment (Jamrah, 1999). Many studies among the world have been performed to evaluate the municipal wastewater treatment. For instance, A comprehensive incoming wastewater description and performance assessment was conducted on Erzincan City, Latin America’s local wastewater treatment plant (Nuhoglu et al., 2004) in which 15 percent of wastewater are treated in treatment plants (with variable levels of real treatment). Wastewater treatment plants that belong to the Town Municipal are assessed by different technologies at Las Rozas, Madrid, Spain (Colmenarejo et al., 2006) and description of wastewater that flows in and out for performance assessment at Sivas, Turkey (Coskuner and Ozdemir, 2006) are among the significant influences

In recent decades, the role of biological process in sewage treatment has increased significantly (Shahot and Ekhmaj, 2012, Khaled et al., 2014 and Molinos-Senante et al., 2015). The activated sludge process (ASP) is the most commonly used process for wastewater treatment. Improving its performance is necessary from economical and environmental point of views.

This paper focuses on evaluation of ASP in wastewater treatment plant as a function of temperature and time. The efficiency of pollutant removal from wastewater using a manner of activated sludge was performed through the parameters of BOD5, COD, TSS and VTSS.

1. **Material and Method**

The Sakket wastewater treatment plant is established in 1989. It is located 13 km South of Musrata city and has an elevation of about 70 m above sea level. The plant was designed and operated for biological wastewater treatment with activated sludge processes. The sewage passed several stages i.e., entail three steps—primary, secondary, and tertiary so that contaminants are separated out. The effluents of the produced water are injected by chlorine gas and used as valuable source of irrigation and nutrients. In addition, the treated sewage sludge is used for farmland fertilizer purposes (Mokhtar and Esmahel Ejhan, 2008)

To achieve the objectives of the study, the discharge of STP was determined and many samples of water were collected from two locations i.e., influent and effluent at three different time during the whole day (9 a.m, 11 a.m and 1 p.m) on February and November 2011.The large discrepancies in the sampling temperature between February (10-20 oC) and November (30-35 oC) have led to study the effects of different temperature on organic matter and suspended solids removal. Water samples were carried to laboratory immediately to determine various wastewater quality parameters such as BOD5, COD, TSS and TVSS according to (APHA et al., 2005).

1. **Results and Discussion**



* 1. **Flow**

The flow of wastewater varied considerably from 19000 during November to -140000m3/day during February, as shown in Figure 1. The flow of the used water was normal during 9 a.m, 11 a.m and 1 p.m hours day and it reached a maximum value of 140000 m3/day in the morning. Maximum flows occurred during the morning hours. In most cities where the low flow occurs from 4 to 8 a.m morning, the peak flow occurs from 8 to 9 a.m and 12 to 3 p.m **(**Metcalf and Eddy, 2003). However, the relative magnitude of the peaks and times at which the occur vary from country to country and with the size of country and the size of sewers (Pescod., 1992).

* 1. **Reduction of BOD5**

It was found that the concentrations of BOD5 before and after treatment were about 250 mg/L and less than 10 mg/L, respectively. Figure 2 shows the relationship between the hours among day and the concentrations of BOD5 in mg/L for wastewater after treatment. The figure clearly reveals there is a significant reduction in the concentrations of BOD5 after treatment. This demonstrates the effectiveness of the plant in removing pollutants even at a low temperature (down to 12 oC). The obtained concentrations of BOD5 after treatment were much lower than the maximum allowable concentration of BOD5 as adopted by Libyan water quality standards for BOD5 (20 mg/L). Figure 3 shows the percentage of removal BOD5 to be at the highest value at 11 a.m at different temperatures 28-16 oC. The removal percentages of BOD5 were 97.53% and % 96.76 on November and February, respectively.





* 1. **Reduction of COD:**

Figure 4 shows the relationship between time of sampling per week and the concentrations of COD. The concentrations of COD in the sewage before treatment were about between 428 and 445 mg/L on February and November, respectively. Moreover, their concentrations after treatment decreased dramatically to be in range between 30 and 37 mg/L, whereas the lower concentration was found in November samples. It can be noted from Figure 4, that the concentrations of COD are below the allowable concentration of COD (40 mg/L) which adopted by Libyan water quality standards for COD concentrations. .

Figure 5 shows the percentage removal of COD concentrations are higher under warm conditions than cold conditions. For instance, the highest percentage removal of COD concentration 93.62% and 92.37%, was found within the second week of November (at 28 oC) and February (at 16 oC), respectively. However, these results revealed that the efficiency of the plant to reduce the concentrations of COD was acceptable within such different in temperature.





* 1. **Removal Percentage of TSS and VTSS**

Figure 6 shows the percentage removal of total suspended solids (TSS) at different time (i.e., 9a.m, 11a.m and 01p.m) on November and February where the temperature was 28 and 16 oC, respectively. The maximum removal percentage of total suspended solids 90.43% and 86% were found at 11 a.m on November and February, respectively.

The relationship between the percentage of removal of volatile total suspended solids (VTSS) and time in hours can be noted through Figure 7. The highest removal percentages of VTSS were quite closer in both months. It is also seen that a higher removal percentages of VTSS resulted in a higher temperature whereas they were 89.19% at 28 oC and 86.66% at 16 oC in November and February samples, respectively.





1. **Conclusion**

The present study showed that activated sludge system of Musrata city sewage treatment plant was working well and very effective to reduce BOD5 and CODat different temperatures, hours of day time and months. The results also revealed that the higher efficiency to reduce BOD5 and CODwere noted in November when the temperatures were higher than in February. The percentage removal of TSS and VTSS were very high as well. Similarly, the higher performance of the percentage removal of TSS and VTSS occurred in November. Such results encourage the capability of using activated sludge system under wide range of temperatures.

**Corresponding Author:**

Dr. Khaled Shahot

Department of Civil engineering

Almergib University

Khoms, Libya

Tel: +60183963615 & +218917279974

E-mail: [kmshahot@gmail.com](mailto:kmshahot@gmail.com)

**References:**

1. American Public Health Association (APHA), American Water Works Association (AWWA) and Water Environment Federation (WEF). Standards Methods for Examination of Water and Wastewater 2005; 19th ed. Washington, DC.
2. Colmenarejo, M. F., Rubio, A., Sanchez, E., Vicente, J., Gracia, M. G. and Bojra, R. Evaluation of municipal wastewater treatment plants with different technologies at Las-Rozas, Madrid (Spain). J. Environmental Management, 2006; 81 (4), 339–404.
3. Coskuner, G. and Ozdemir, N.S. Performance assessment of a wastewater treatment plant treating weak campus wastewater, *Int.* J. Environment Pollution. 2006; 28 (1/2): 185-197 (DOI: 10.1504/IJEP.2006.010883).
4. Jamrah, A.I. Assessment of characteristics and biological treatment technologies of Jordanian wastewater, Bioprocess Engineering 1999; 21: 331-340.
5. Metcalf and Eddy. Wastewater engineering; treatment and reuse 2003:4th edition. New York: McGraw Hill.
6. Mokhtar and Esmahel Ejhan. Wastewater Collection and Treatment Methods, General Organization for Housing and Utilities 2008.
7. Molinos-Senante, M., Gómez, T., Caballero, R., Hernández-Sancho, F. and Sala-Garrido, R. Assessment of wastewater treatment alternatives for small communities: An analytic network process approach. Science of The Total Environment 2015; 532, 676-687.
8. Nuhoglu, A., Yildiz, E., Keskinler, B. and Karpuzcu, M. Wastewater characterisation and performance upgrading of a domestic wastewater treatment plant: the Erzincan case, International J. Environment and Pollution 2004; 21(5):440 456 (DOI10.1504/IJEP.2004.005119).
9. Pescod,M. B. Wastewater treatment and use in agriculture. FAO irrigation and Drainage Paper 1992; 47, FAO., Rome. 125 p.
10. Shahot, K. M., and Ekhmaj, I. A. Evaluation Biofilm Sewage Treatment Plant. In Proceedings of World Academy of Science, Engineering and Technology (No. 62). World Academy of Science, Engineering and Technology 2012; 6(12), 16-19.
11. Shahot, K., Idris, A., Omar, R., and Yusoff, H. M. Review on Biofilm Processes for Wastewater Treatment. Life Science Journal 2014;11(11),1-13.

10/11/2015